## tiers
code | name | availability_target | typical_use | notes
I | Basic capacity | 99.671% | Lab/dev, non-critical edge | Single path, no redundancy; planned shutdowns required
II | Redundant components | 99.741% | Small enterprise rooms | Single distribution path, N+1 components
III | Concurrent maintainable | 99.982% | Colo/hyperscale blocks | Multiple paths; any one component can be maintained without downtime
IV | Fault tolerant | 99.995% | Financial/mission critical | Fully redundant, independent paths; withstands worst‑case single failure

## redundancy
name | layer | description | pros | cons | typical_use
N | power | Exact capacity equals load | High efficiency, low cost | No fault tolerance | Test/dev, non-critical
N+1 | power | One extra module beyond N | Tolerates single fault | More CapEx/space | Most colocation suites
2N | power | Two independent full-capacity paths | High resilience | High CapEx/OpEx | Trading floors, FT workloads
2(N+1) | power | Two paths, each N+1 modular | Maintenance + fault safe | Complexity | Large campuses
N+1 | cooling | One extra chiller/CRA(H) beyond demand | Maintenance flexibility | Partial redundancy | Common enterprise
2N | cooling | Dual plants or loops | Plant-level resilience | High cost | Tier IV aspirations

## cooling_methods
name | liquid? | free_cooling? | density_suitable(kW/rack) | notes
CRAC (DX) | FALSE | FALSE | 5 | Direct expansion coil; compact; suitable for small rooms
CRAH (chilled water) | FALSE | FALSE | 15 | Coil fed by chiller plant; scalable; pairs with economizer
Air economizer | FALSE | TRUE | 10 | Uses outdoor air to reduce compressor energy; filtration needed
Glycol dry cooler | FALSE | TRUE | 15 | Dry coolers with glycol mix; freeze protection
Evaporative condenser | FALSE | TRUE | 15 | Adiabatic assistance for hot/dry climates; watch WUE
Rear door heat exchanger | FALSE | FALSE | 25 | Row-level coil that intercepts hot air at rack exit
Cold plates (D2C) | TRUE | FALSE | 50 | Direct-to-chip liquid for CPUs/GPUs; manifolds required
Single-phase immersion | TRUE | FALSE | 80 | Dielectric bath; pumped loop; high density
Two-phase immersion | TRUE | FALSE | 100 | Boiling dielectric; highest heat flux; specialized fluids

## lifecycle_phases
phase | key_decisions | key_risks | primary_inputs | typical_owners
Site selection | Power lead-time, fiber routes, land use, water, incentives | Entitlement delays, interconnect risk, climate hazards | Load forecast, utility queue, metro fiber map, permitting path | Developer, utility, carriers
Entitlements | Zoning, environmental, interconnect applications | Appeals, conditions, timeline slips | Site surveys, studies, agency meetings | Developer, counsel, AHJs
Design | Topology, density roadmap, cooling approach | Over/under-spec, supply chain | Basis of design, vendor selections, controls | A/E, owner, operators
Construction | Phasing, logistics, long-lead equipment | Change orders, safety, QA | Submittals, FATs, method statements | GC, trades, owner rep
Commissioning | L1–L5 testing, IST, documentation | Defects found late, retests | Test scripts, load banks, as-builts | CxA, OEMs, ops
Operations | Capacity, maintenance, incidents, energy | Unplanned downtime, aging assets | CMMS/DCIM data, MOP/SOP/EOP | Site ops, vendor PM, customers

## roles
role | org_type | primary_goals | buy_signals | objections
Real estate lead | Developer/Operator | Secure land/power/fiber at right cost and timeline | Utility LOIs, substation plans, IX presence | High land cost; slow utility queue
Design engineer (EE) | A/E Firm | Select safe, efficient electrical topology and protection | Tier objective, density, arc-flash limits | Cost, footprint, lead times
Design engineer (ME) | A/E Firm | Design cooling plant and distribution for target density | Climate hours, water policy, liquid-ready | WUE, Legionella, water rights
Construction PM | GC | Deliver on time/quality within budget | Long-lead tracking, FAT dates | Change orders, weather
Commissioning agent | CxA | Validate systems performance and fault response | Test scripts, IST windows | Retest costs, vendor availability
Site operations lead | Operator | Run safely and meet SLAs | PM schedules, spares, NOC alerts | Access conflicts, outage windows
Network architect | Operator/ISP | Assure diverse fiber and IX options | Conduit routes, MMR density | ROW delays, carrier SLAs
Customer DC lead | Tenant | Meet compute growth and resilience targets | kW commit, cross-connects | Price escalators, CX lead times

## metrics
metric | definition | unit | good_range | notes
PUE | Total facility energy / IT energy | ratio | <=1.3 new‑build (climate‑dependent) | Track trend; beware partial metering
WUE | Annual water use / IT energy | L/kWh | As low as practical; policy‑driven | Adiabatic tradeoffs
Rack density | Power allocated per rack | kW/rack | 10–30 typical; 30–80+ for AI/HPC | Drives cooling choice
Cross‑connect price | Monthly fee per L1 interconnect | USD/mo | Market‑dependent | Impacts ecosystem stickiness
Time‑to‑power | Months from LOI to first MW usable | months | <=18 desired | Utility queue critical
Generator run time | Fuel autonomy at full critical load | hours | >=24 baseline | Depends on refuel SLAs
Fiber diversity | Count of physically diverse routes | count | >=2 preferred | Verify true path separation

## markets_US
code | market_name | notes
IAD | Northern Virginia (Loudoun/Prince William/Fairfax) | Largest global hub; dense fiber; utility queue is gating factor
DFW | Dallas–Fort Worth | Land and incentives; fast growth; multiple utilities
PHX | Phoenix (Mesa/Chandler/Goodyear) | Hot/dry; strong economizer hours; water mgmt critical
ATL | Atlanta | Enterprise base; diverse carriers; substation planning
SJE | Santa Clara / San Jose | Scarce land; high cost; top-tier IX ecosystem
SEA | Seattle | Cloud presence; hydro power context; seismic considerations
PDX | Portland/Hillsboro | Hyperscale growth; trans‑Pacific cables; incentives
CHI | Chicago/Elk Grove | Major Midwest hub; multi‑utility; strong MMR density
SAT | San Antonio | Growth corridor; land and power availability improving
RIC | Richmond | Edge of NoVA sphere; power cost and land optionality
CLT | Charlotte | Financial services presence; developing interconnection
DEN | Denver | Central U.S. reach; altitude/cooling context
LAS | Las Vegas | Dry climate; land availability; water constraints
MIA | Miami | Subtropical; hurricane design and Latin America routes